## Sheet1
Transformer Oil Report
Client: |  | Gainesville Renewable Energy Center
Unit Identification: |  | ELA-XF-1006 |  |  | Unit Description: | SN 12JC596260002
|  | Sample ID | Sample ID | Sample ID | Sample ID | Sample ID | Sample ID | Sample ID
Lab Number |  | 525816 | 529918 | 533185 | 572975 | 619487 | 635850 | 654172
Sample Date |  | 2013-12-18 | 2014-02-06 | 2014-02-26 | 2015-02-05 | 2016-02-24 | 2016-08-16 | 2017-02-07
Parameter | Units
Dielectric Stength (D877) | kV | 54 | 48 | 53 | 54 | 47 | 38 | 52
TAN (D974) | mg KOH/g | 0.016 | 0.016 | 0.018 | 0.01 | 0.024 | 0.018 | 0.02
Interfacial Tension (D971) | mN/m | 34.3 | 34.7 | 34.7 | 31.9 | 37.3 | 40 | 34.6
Color (D1500) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Visual (D1524) |  | Clear | Slight Particulate | Clear | Clear | Clear | Clear | Clear
Specific Gravity (D1298) | g/ml | 0.871 | 0.875 | 0.876 | 0.874 | 0.872 | 0.87 | 0.876
Water (D1533) | ppm | 16 | 17 | 11 | 4 | 6 | 5 | 3
Class |  | Good | Good | Good | Good | Good | Good | Good
Corrosive Sulfur (D1275B) |  | 2014-02-26: NC 1a; 2016-02-24: NC 3a; 2016-08-16: NC 1b; 2017-02-07: NC 1b
Recommended Service:
Retest 1 year.
Dissoved Gases
Hydrogen (H2) | ppm | 102 | 97 | 109 | 71 | 86 | 93 | 83
Methane (CH4) | ppm | 6 | 13 | 10 | 8 | 9 | 10 | 11
Ethylene (C2H4) | ppm | 9 | 15 | 7 | 5 | 6 | 6 | 6
Ethane (C2H6) | ppm | 7 | 7 | 2 | 2 | 3 | 2 | 3
Acetylene (C2H2) | ppm | 2 | 3 | 2 | 1 | 1 | 1 | 0
Carbon Monoxide (CO) | ppm | 352 | 298 | 306 | 318 | 419 | 513 | 520
Total Combined Gas | ppm | 478 | 433 | 436 | 405 | 524 | 625 | 623
Carbon Dioxide (CO2) | ppm | 827 | 706 | 1192 | 1055 | 1424 | 1844 | 1868
Nitrogen (N2) | ppm | 67181 | 66810 | 68077 | 52144 | 51461 | 56341 | 60991
Oxygen (O2) | ppm | 11183 | 11782 | 9682 | 6402 | 5369 | 4521 | 6831
Total Dissolved Gas | Percent | 8 | 8 | 7.9 | 6 | 5.9 | 6.3 | 7
Discussion of Results:
Combustible gases indicate cellulose breakdown may be occurring due to overheating of XFMR
insulation by over loading the equipment or where normal circulation is impaired and high temps
result in XFMR. Retest 1 year.