## Sheet1
Transformer Oil Report
Client: |  | Gainesville Renewable Energy Center
Unit Identification: |  | ELA-XF-1007 |  |  | Unit Description: | SN 12JC596270001
|  | Sample ID | Sample ID | Sample ID | Sample ID | Sample ID | Sample ID | Sample ID
Lab Number |  | 525817 | 529920 | 533186 | 572976 | 619488 | 635851 | 654173
Sample Date |  | 2013-12-18 | 2014-02-06 | 2014-02-26 | 2015-02-05 | 2016-02-24 | 2016-08-16 | 2017-02-07
Parameter | Units
Dielectric Stength (D877) | kV | 53 | 49 | 57 | 57 | 38 | 42 | 46
TAN (D974) | mg KOH/g | 0.012 | 0.016 | 0.016 | 0.02 | 0.02 | 0.03 | 0.024
Interfacial Tension (D971) | mN/m | 36.3 | 33.6 | 33.5 | 33.9 | 37.6 | 39.7 | 33.1
Color (D1500) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.5
Visual (D1524) |  | Clear | Clear | Clear | Clear | Clear | Clear | Clear
Specific Gravity (D1298) | g/ml | 0.871 | 0.875 | 0.875 | 0.874 | 0.87 | 0.87 | 0.876
Water (D1533) | ppm | 15 | 16 | 10 | 2 | 6 | 8 | 6
Class |  | Good | Good | Good | Good | Good | Good | Good
Corrosive Sulfur (D1275B) |  | 2014-02-26: NC 3a; 2016-02-24: NC 3a; 2016-08-16: NC 1b; 2017-02-07: NC 1b
Recommended Service:
Retest 1 year.
Dissoved Gases
Hydrogen (H2) | ppm | 59 | 67 | 74 | 54 | 65 | 63 | 62
Methane (CH4) | ppm | 6 | 9 | 9 | 8 | 9 | 9 | 10
Ethylene (C2H4) | ppm | 6 | 10 | 5 | 4 | 5 | 5 | 5
Ethane (C2H6) | ppm | 3 | 8 | 2 | 2 | 3 | 2 | 3
Acetylene (C2H2) | ppm | 0 | 0 | 0 | 0 | 0 | 0 | 0
Carbon Monoxide (CO) | ppm | 179 | 226 | 211 | 262 | 333 | 382 | 398
Total Combined Gas | ppm | 253 | 320 | 301 | 330 | 415 | 461 | 478
Carbon Dioxide (CO2) | ppm | 541 | 529 | 1056 | 1148 | 1554 | 1815 | 1968
Nitrogen (N2) | ppm | 63806 | 66697 | 66355 | 51649 | 48633 | 54075 | 57318
Oxygen (O2) | ppm | 13475 | 14167 | 11390 | 8577 | 6800 | 6922 | 8734
Total Dissolved Gas | Percent | 7.8 | 8.2 | 7.9 | 6.2 | 5.7 | 6.3 | 6.8
Discussion of Results:
Combustible gases indicate cellulose breakdown may be occurring due to overheating of XFMR
insulation by over loading the equipment or where normal circulation is impaired and high temps
result in XFMR. Retest 1 year.