## Sheet1
Transformer Oil Report
Client: |  | Gainesville Renewable Energy Center
Unit Identification: |  | ELA-XF-1008 |  |  | Unit Description: | SN 12JC596270002
|  | Sample ID | Sample ID | Sample ID | Sample ID | Sample ID | Sample ID | Sample ID
Lab Number |  | 525818 | 529921 | 533187 | 572977 | 619489 | 635852 | 654174
Sample Date |  | 2013-12-18 | 2014-02-06 | 2014-02-26 | 2015-02-05 | 2016-02-24 | 2016-08-16 | 2017-02-07
Parameter | Units
Dielectric Stength (D877) | kV | 56 | 48 | 52 | 54 | 45 | 45 | 47
TAN (D974) | mg KOH/g | 0.012 | 0.016 | 0.016 | 0.02 | 0.016 | 0.026 | 0.016
Interfacial Tension (D971) | mN/m | 35.2 | 33.1 | 35.7 | 33.7 | 36.5 | 37.3 | 31.2
Color (D1500) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Visual (D1524) |  | Clear | Clear | Clear | Clear | Clear | Clear | Clear
Specific Gravity (D1298) | g/ml | 0.872 | 0.874 | 0.875 | 0.874 | 0.872 | 0.87 | 0.872
Water (D1533) | ppm | 15 | 16 | 9 | 6 | 5 | 5 | 3
Class |  | Good | Good | Good | Good | Good | Good | Good
Corrosive Sulfur (D1275B) |  | 2014-02-26: NC 1b; 2016-02-24: NC 3a; 2016-08-16: NC 1b; 2017-02-07: NC 3a
Recommended Service:
Retest 1 year.
Dissoved Gases
Hydrogen (H2) | ppm | 53 | 46 | 54 | 45 | 44 | 51 | 44
Methane (CH4) | ppm | 3 | 6 | 3 | 6 | 6 | 9 | 11
Ethylene (C2H4) | ppm | 7 | 5 | 2 | 6 | 7 | 13 | 15
Ethane (C2H6) | ppm | 2 | 5 | 1 | 2 | 3 | 3 | 3
Acetylene (C2H2) | ppm | 0 | 0 | 0 | 0 | 0 | 0 | 0
Carbon Monoxide (CO) | ppm | 179 | 190 | 187 | 315 | 348 | 458 | 444
Total Combined Gas | ppm | 244 | 252 | 247 | 374 | 408 | 534 | 517
Carbon Dioxide (CO2) | ppm | 318 | 267 | 853 | 1174 | 1397 | 1663 | 1777
Nitrogen (N2) | ppm | 70053 | 67990 | 69142 | 57936 | 46714 | 57451 | 58459
Oxygen (O2) | ppm | 15088 | 15924 | 12652 | 3618 | 7379 | 6959 | 9310
Total Dissolved Gas | Percent | 8.6 | 8.4 | 8.3 | 6.3 | 5.6 | 6.7 | 7
Discussion of Results:
Combustible gases indicate cellulose breakdown may be occurring due to overheating of XFMR
insulation by over loading the equipment or where normal circulation is impaired and high temps
result in XFMR. Retest 1 year.