## Sheet1
Transformer Oil Report
Client: |  | Gainesville Renewable Energy Center
Unit Identification: |  | EMA-XF-1001 SST |  |  | Unit Description: | SN C-07992-5-1
|  | Sample ID | Sample ID | Sample ID | Sample ID | Sample ID | Sample ID | Sample ID
Lab Number |  | 525819 | 529919 | 533188 | 572978 | 619490 | 635853 | 654175
Sample Date |  | 2013-12-18 | 2014-02-06 | 2014-02-26 | 2015-02-05 | 2016-03-17 | 2016-08-16 | 2017-02-07
Parameter | Units
Dielectric Stength (D877) | kV | 57 | 49 | 57 | 51 | 53 | 44 | 56
TAN (D974) | mg KOH/g | 0.012 | 0.012 | 0.01 | 0.014 | 0.02 | 0.02 | 0.02
Interfacial Tension (D971) | mN/m | 38.8 | 41.5 | 42.8 | 36.2 | 43.4 | 46.6 | 39.6
Color (D1500) |  | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Visual (D1524) |  | Clear | Clear | Clear | S/Pt | Clear | Clear | Clear
Specific Gravity (D1298) | g/ml | 0.88 | 0.884 | 0.886 | 0.884 | 0.88 | 0.881 | 0.88
Water (D1533) | ppm | 14 | 18 | 11 | 18 | 7 | 12 | 8
Class |  | Good | Good | Good | Good | Good | Good | Good
Corrosive Sulfur (D1275B) |  | 2014-02-26: NC 3a; 2016-03-17: NC 3a; 2016-08-16: NC 1b; 2017-02-07: NC 3a
Recommended Service:
Retest 1 year.
Dissoved Gases
Hydrogen (H2) | ppm | 17 | 12 | 38 | 30 | 4 | 5 | 4
Methane (CH4) | ppm | 5 | 0 | 3 | 4 | 4 | 5 | 5
Ethylene (C2H4) | ppm | 3 | 5 | 2 | 3 | 2 | 2 | 3
Ethane (C2H6) | ppm | 1 | 0 | 0 | 1 | 1 | 0 | 1
Acetylene (C2H2) | ppm | 0 | 0 | 0 | 0 | 0 | 0 | 0
Carbon Monoxide (CO) | ppm | 258 | 225 | 262 | 294 | 368 | 484 | 399
Total Combined Gas | ppm | 284 | 242 | 305 | 332 | 379 | 496 | 412
Carbon Dioxide (CO2) | ppm | 552 | 655 | 926 | 1243 | 1992 | 2253 | 2252
Nitrogen (N2) | ppm | 49330 | 67641 | 51260 | 47484 | 4065 | 48205 | 55463
Oxygen (O2) | ppm | 15489 | 19978 | 12542 | 9294 | 12329 | 8588 | 14497
Total Dissolved Gas | Percent | 6.6 | 8.9 | 6.5 | 5.8 | 5.5 | 6 | 7.3
Discussion of Results:
Combustible gases indicate cellulose breakdown may be occurring due to overheating of XFMR
insulation by over loading the equipment or where normal circulation is impaired and high temps
result in XFMR. Retest 1 year.