## Slide 1: The Development and Construction of a 100 MW Biomass Power Plant Gainesville, Florida
A project overview by
Leonard Fagan
Vice President of Engineering
Energy Management, Inc.

## Slide 2: Ownership Structure
GREC is a limited partnership between:
and
Fagen Principals

## Slide 3: Project Description
100 MW biomass-fired generating facility
  Metso HYBEXTM Bubbling Fluidized Bed (BFB) boiler will combust wood waste fuel to produce superheated steam
Primary fuels are wood and wood waste
  Forest, mill, and agricultural residues; waste pallets;
  urban wood waste; thinning's; slash; and storm debris
  Efficient and clean design
  Low heat rate due to advanced boiler design and steam cycle
  Low emissions through clean combustion process
    SCR to reduce NOx emissions
    Baghouse to reduce particulate emissions
    Sorbent injection for acid gas reduction
Located in Gainesville, Florida
  Well-positioned to capture fuel resource from north central Florida wood basket, as well as urban wood waste in region
  Co-located with existing coal facility
  Utilizing groundwater and reclaimed water for process water needs

## Slide 4: Overall Layout

## Slide 5: History & Schedule
Date | Description
December 2006 | Submitted letter of interest to GRU in response to RFI
December 2007 | Submitted proposal to GRU in response to RFP
January 2008 | Invited by Gainesville City Commission to submit final proposal
April 2008 | Submitted final proposal to GRU
May 2008 | Awarded right to solely negotiate power purchase agreement (PPA) with GRU
April 2009 | Executed 30-year PPA with GRU
September 2009 | Executed long-term lease with City of Gainesville for 131-acre parcel adjacent to coal plant

## Slide 6: Development Timeline
  May 2009 Initiated preliminary design & permitting
  December 2010 Final permit approval from FDEP
  March 2011 Construction start date with LNTP
  June 30, 2011 Financial closing and FNTP
  October 16, 2013 Achieved Substantial Completion
  December 17, 2013 Began Commercial Operation

## Slide 7: Milestones
Milestone | Completion Date
Boiler Hydro | February 21, 2013
First Fuel Delivery | April 3, 2013
Start of Sustained Wood Delivery | June 10, 2013
Chemical Clean | June 18, 2013
First Fire – Natural Gas | July 7, 2013
First Fire – Biomass | July 8, 2013
Steam Blows & Restoration | July 22, 2013
First Sync to Grid | August 16, 2013
Full Load Operation | August 20, 2013
Substantial Completion | October 16, 2013
Performance Tests | November 23, 2013
Commercial Operation | December 17, 2013

## Slide 8: Key Partners
Fagen, Inc. EPC Contractor
Zachry Engineering
Metso BFB Boiler
Metso Automation DCS
Clyde Bergemann Bag House & DSI
Siemens Steam Turbine
Wolf Material Handling Wood yard design & Supply
Aquatech Water Treatment (demin & ZLD)
Trace Environmental CEMS
Flowserve Major pumps

## Slide 9: Design Concepts
102.5 MW Net (116.1 MW Gross)
High Availability
20 Days Fuel Supply
Low Heat Rate
Utility Quality
Zero Liquid Discharge Site
138-kV Interconnect

## Slide 10: Cycle Design
1620 psig 1005oF superheater outlet
4 STG bleeds for feed water heating
440oF feed water to economizer
2.4 in hg abs design condenser vacuum
Fuel moisture 50% design, 45% guarantee, 41% average
Optimized auxiliary power
Low net heat rate

## Slide 11: Heat Balance

## Slide 12: Metso Boiler
Bubbling fluidized bed boiler
930,000 pph, 1,620 psig/1005 o F designed for 50% moisture fuel
Similar to Nacogdoches design through economizer
Natural gas start up burners
Hot baghouse (450oF operational temperature)
Sorbent injection using Sodium Bicarbonate
Low dust SCR Catalyst by Ceram
Metso provided design, supply and erection of boiler island

## Slide 13: Project Description
Metso HYBEX boiler Bubbling Fluidized Bed (BFB) technology
Steam: 292 MWth (100 MWe) 930,000 lbs/hr 1645 psi 1005 °F
Boiler: Similar to Nacogdoches design
  Stainless finishing superheater Hydrobeam bottom

## Slide 14: Project Description
GREC: World’s largest BFB with
lowest flue gas emissions
Fulfills EPA’s most recent flue gas emission limits
SCR for NOx emissions
Baghouse filters with dry sorbent feeding

## Slide 15
Fluidization

## Slide 16: Siemens Steam Turbine
SST900 condensing steam turbine generator
Made in Finspong, Sweden
1,575 psig 1,000o F rated at 116.1 MW
Axial exhaust condensing at 2.4 in Hg Abs
4 heater bleeds
Brush 136.6 MVA, 13.8 kV TEWAC generator

## Slide 17: Plant Control
DCS – Metso Automation DNA
BFB Boiler monitoring and control
HIMA integrated into DCS for start-up burners
BOP
Advanced boiler controls optimization
AGC
Coordinated control
Training simulator
Wood yard PLC with control room HMI
Siemens STG PLC
Aquatech water treatment PLC
CEMS PLC with computer in control room

## Slide 18: Control & DCS Rooms

## Slide 19: Aerial View

## Slide 20: View from West

## Slide 21: View from SE

## Slide 22: View of Wood Yard

## Slide 23
Truck Tippers

## Slide 24
Trucks Tipping

## Slide 25: Stacker Reclaimer

## Slide 26: Wagner at Work

## Slide 27: Wagner at Work

## Slide 28
GREC will need approximately 1 million green tons of biomass fuel per year
Urban Wood
  Clean wood waste consisting of urban tree debris from tree surgeons, municipal brush, pallets
  No construction and demolition debris or municipal solid waste will be utilized
Forest Biomass
  Low-value trees, tree tops, and branches remaining after commercial tree harvest and land clearing
Mill Residues
  Residues from primary and secondary wood processing (bark, saw dust, shavings, scraps, and wood chips)
Fuel Sources

## Slide 29: O & M
GREC has subcontracted to NAES Corporation to operate and maintain the plant on a 24/7 basis. NAES has 41 full-time employees working at GREC.
Lead Control Room Operator (4)
Operations Supervisor
Steven Marsh
Plant Manager
Russell Abel
Maintenance Supervisor
Tommy Gardner
Administrative Assistant
Maintenance Planner
Maintenance Technician
(4)
IC&E Technician (3)
Water Treatment Operator (4)
Auxiliary Plant Operator
(8)
Fuel Yard Operator (10)
Plant Engineer
Ali Leaphart
Warehouse Technician
Office Supervisor
Lorie Thebaut

## Slide 30: Fuel Procurement
GREC has subcontracted to BioResource Management, Inc. (BRM) to manage fuel procurement and ensure forest sustainability standards are met.
BRM is a Gainesville-based consulting firm that specializes in biomass supply services
BRM has 4 full-time employees on site: Biomass Procurement Manager, Quality Control Manager, Accounts Manager and Field Forester

## Slide 31: Construction Challenges
High water table
Extensive dewatering
1200 augur cast piles
Average grade build-up of 3 feet

## Slide 32
Early Construction
Conveyor Tunnel Rebar – Sept 2011
Conduit Installation – Oct 2011

## Slide 33
Early Construction
Aerial View – March 2012

## Slide 34: Emissions Challenges
Low Dust SCR for NOx Control (hot bag house)
Sorbent injection for HCl, HF and SAM (sodium bicarbonate)
Low levels of HCl and HF pushing measuring limits
IB MACT addition of Hg and low PM

## Slide 35: View of Baghouse

## Slide 36: Zero Discharge Site
Boiler blowdown, RO & filter backwash & miscellaneous sumps to cooling tower basin
Cooling tower blowdown to 80,000-gallon waste water tank
Aquatech ZLD system design and supply
Vertical tube falling film evaporator sized for 165 gpm
Forced circulation crystallizer
Distillate back to process water system
Crystallizer belt filter press
Salt cake to landfill

## Slide 37: Zero Discharge System

## Slide 38: Performance Tests
Overview of Performance Test Results
Continuous Emissions Monitoring System (CEMS)
certification is complete.
Heat Rate Performance Test:
Tested Capacity – 102.5 MW
Tested Heat Rate – 3% below Guarantee
Emission Testing – All Passed

## Slide 39: Thank you for your interest. www.gainesvillebiomass.com